##### EXAMPLE

##### EXAMPLE OF GREASE INTERCEPTOR SIZING FORMULA

Project Name: Fast Food

Address:  Colorado Springs

Project #:  2010-CXXX

- Determine maximum drainage flow from fixtures:

| Type of Fixture | Flow Rate | No. of Fixtures | Flow Rate x No. of Fixtures |
| --- | --- | --- | --- |
| Mop sink | 20 gpm |  |  |
| Single compartment sink | 20 gpm | 4 | 80 |
| Single compartment sink with garbage disposal | 35 gpm |  |  |
| Double compartment sink | 25 gpm |  |  |
| Triple compartment sink | 35 gpm | 1 | 35 |
| Up to 30 gal. dishwasher | 15 gpm |  |  |
| 30 gal. To 50 gal. dishwasher | 25 gpm |  |  |
| Larger than 50 gal. dishwasher | 40 gpm |  |  |
| B. Total flow rate = | 115 |

Loading Factors (Definitions of restaurants as per section 9.07(a)):

Low Volume – Take Out = 0.02

Low Volume – Sit Down = 0.09

Medium Volume – Fast Food = 0.10

Medium Volume – Sit Down = 0.10

High Volume = 0.11

(B) x (C) = avg. flow per minute

= 115 gpm x 0.10 = 11.5 gpm

(D) x 60 min. = avg. flow per hour

= 11.5 gpm x 60 min = 690 gph

## F. (E)	x 2 hours retention time = volume of interceptor in gallons

## = 690 gph x 2 hrs = 1380 gal